## Portada
MÉTODO DEL GRADIENTE HIDRÁULICO
Solución de un ejercicio del Método del Gradiente Hidráulico para comprobar resultados de MGH
Autor: Ing. Carlos Camacho Soto, ccamacho@segundafundacion.com
Lugar: San José, Costa Rica
Fecha: julio 2022
Copyright © 2022 Carlos Camacho Soto, ccamacho@segundafundacion.com
This file "GradienteHidráulico.xlsx" is part of mgh
mgh is free software: you can redistribute it and/or modify it under the terms of the GNU General Public License as published by the Free Software Foundation, either version 3 of the License, or (at your option) any later version.
mgh is distributed in the hope that it will be useful, but WITHOUT ANY WARRANTY; without even the implied warranty of MERCHANTABILITY or FITNESS FOR A PARTICULAR PURPOSE.
See the GNU General Public License for more details.
You should have received a copy of the GNU General Public License along with mgh. If not, see <https://www.gnu.org/licenses/>.
Diagrama de la red de prueba a modelar en MGH | Datos de la red de prueba
Nudos de carga fija
| Nudo | Elevación | Carga
| 1 | 90 | 100
Resultados
Nudos de demanda
| Nudo | Elevación | Demanda |  |  |  | Alturas piezométricas |  | Presiones
| 2 | 90 | 60 |  |  |  | 93.5975 | m | 3.5975 | mca
| 3 | 90 | 40 |  |  |  | 82.8569 | m | -7.1431 | mca
| 4 | 90 | 30 |  |  |  | 83.2982 | m | -6.7018 | mca
| 5 | 90 | 30 |  |  |  | 90.612 | m | 0.61205 | mca
| 6 | 90 | 40 |  |  |  | 96.9907 | m | 6.9907 | mca
Tramos de tubería
| Tramo | de→a | L | D | ks | kL | Caudales en tramos
| 0 | '1 – 2 | 0.25 | 500 | 1.5e-06 | 0 | 106.6811 | l/s
| 1 | 2 – 3 | 0.15 | 400 | 1.5e-06 | 10 | 36.5194 | l/s
| 2 | 3 – 4 | 0.1 | 200 | 1.5e-06 | 0 | 3.4806 | l/s
| 3 | 4 – 5 | 0.15 | 400 | 1.5e-06 | 0 | 33.4806 | l/s
| 4 | 2 – 5 | 0.1 | 200 | 1.5e-06 | 0 | 10.1617 | l/s
| 5 | 5 – 6 | 0.2 | 600 | 1.5e-06 | 0 | 53.3189 | l/s
| 6 | 1 – 6 | 0.25 | 300 | 1.5e-06 | 0 | 93.3189 | l/s
Unidades y descripción de variables
| Elevación (topográfica) [m] |  |  | L=Longitud [m]
| Carga (piezométrica) [m] |  |  | D=Diámetro [mm]
| Demanda [l/s] |  |  | ks=Rugosidad [m]
kL=Coeficiente de pérdidas locales [adim]

## I1
Método del gradiente hidráulico. Iteración inicial
Tramo | D | L | ks | km | A
1-2 | 0.25 | 500 | 1.5e-06 | 0 | 0.049087
2-3 | 0.15 | 400 | 1.5e-06 | 10 | 0.017671
3-4 | 0.1 | 200 | 1.5e-06 | 0 | 0.007854
4-5 | 0.15 | 400 | 1.5e-06 | 0 | 0.017671
2-5 | 0.1 | 200 | 1.5e-06 | 0 | 0.007854
5-6 | 0.2 | 600 | 1.5e-06 | 0 | 0.031416
1-6 | 0.25 | 300 | 1.5e-06 | 0 | 0.049087
A12 Topología de la red (tramos) | [7 empty] | A10 Nodos con carga fija |  |  | N coeficiente de pérdidas
NT / NN | 1 | 2 | 3 | 4 | 5 | 6 |  | NT | NUDO | CARGA
1 | -1 | 1 | 0 | 0 | 0 | 0 |  | 1 | -1 | 100 | 2 | 0 | 0 | 0 | 0 | 0 | 0
2 |  | -1 | 1 | 0 | 0 | 0 |  | 2 | 0 |  | 0 | 2 | 0 | 0 | 0 | 0 | 0
3 |  | 0 | 1 | -1 | 0 | 0 |  | 3 | 0 |  | 0 | 0 | 2 | 0 | 0 | 0 | 0
4 |  | 0 | 0 | 1 | -1 | 0 |  | 4 | 0 |  | 0 | 0 | 0 | 2 | 0 | 0 | 0
5 |  | -1 | 0 | 0 | 1 | 0 |  | 5 | 0 |  | 0 | 0 | 0 | 0 | 2 | 0 | 0
6 |  | 0 | 0 | 0 | 1 | -1 |  | 6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 2 | 0
7 | -1 | 0 | 0 | 0 | 0 | 1 |  | 1 | -1 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 2
A21 Transpuesta de A12 | [7 empty] | q Consumos |  |  | Matriz identidad
1 | -1 | 0 | 0 | -1 | 0 | 0 |  | 2 | 0.06 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
0 | 1 | 1 | 0 | 0 | 0 | 0 |  | 3 | 0.04 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0
0 | 0 | -1 | 1 | 0 | 0 | 0 |  | 4 | 0.03 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0
0 | 0 | 0 | -1 | 1 | 1 | 0 |  | 5 | 0.03 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | -1 | 1 |  | 6 | 0.04 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1
Tubería | Q | v | Re | f | hf | hm | hf+hm | alpha
1-2 | 0.1 | 2.0372 | 446750.7175 | 0.013449 | 5.6896 | 0 | 5.6896 | 568.9574
2-3 | 0.1 | 5.6588 | 744584.5291 | 0.012411 | 54.018 | 16.3214 | 70.3394 | 7033.9401
3-4 | 0.1 | 12.7324 | 1116876.7936 | 0.011781 | 194.6862 | 0 | 194.6862 | 19468.6206
4-5 | 0.1 | 5.6588 | 744584.5291 | 0.012411 | 54.018 | 0 | 54.018 | 5401.8046
2-5 | 0.1 | 12.7324 | 1116876.7936 | 0.011781 | 194.6862 | 0 | 194.6862 | 19468.6206
5-6 | 0.1 | 3.1831 | 558438.3968 | 0.012965 | 20.0867 | 0 | 20.0867 | 2008.6666
1-6 | 0.1 | 2.0372 | 446750.7175 | 0.013449 | 3.4137 | 0 | 3.4137 | 341.3744
A11
56.8957 | 0 | 0 | 0 | 0 | 0 | 0
0 | 703.394 | 0 | 0 | 0 | 0 | 0
0 | 0 | 1946.8621 | 0 | 0 | 0 | 0
0 | 0 | 0 | 540.1805 | 0 | 0 | 0
0 | 0 | 0 | 0 | 1946.8621 | 0 | 0
0 | 0 | 0 | 0 | 0 | 200.8667 | 0
0 | 0 | 0 | 0 | 0 | 0 | 34.1374
A11'
56.8957 | 0 | 0 | 0 | 0 | 0 | 0
0 | 703.394 | 0 | 0 | 0 | 0 | 0
0 | 0 | 1946.8621 | 0 | 0 | 0 | 0
0 | 0 | 0 | 540.1805 | 0 | 0 | 0
0 | 0 | 0 | 0 | 1946.8621 | 0 | 0
0 | 0 | 0 | 0 | 0 | 200.8667 | 0
0 | 0 | 0 | 0 | 0 | 0 | 34.1374
N * A11'
113.7915 | 0 | 0 | 0 | 0 | 0 | 0
0 | 1406.788 | 0 | 0 | 0 | 0 | 0
0 | 0 | 3893.7241 | 0 | 0 | 0 | 0
0 | 0 | 0 | 1080.3609 | 0 | 0 | 0
0 | 0 | 0 | 0 | 3893.7241 | 0 | 0
0 | 0 | 0 | 0 | 0 | 401.7333 | 0
0 | 0 | 0 | 0 | 0 | 0 | 68.2749
R = inversa de (N * A11')
0.008788 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0.00071084 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0.00025682 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0.00092562 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0.00025682 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0.0024892 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0.014647
M= A21 / (N A11')
0.008788 | -0.00071084 | 0 | 0 | -0.00025682 | 0 | 0
0 | 0.00071084 | 0.00025682 | 0 | 0 | 0 | 0
0 | 0 | -0.00025682 | 0.00092562 | 0 | 0 | 0
0 | 0 | 0 | -0.00092562 | 0.00025682 | 0.0024892 | 0
0 | 0 | 0 | 0 | 0 | -0.0024892 | 0.014647
C =A21 / (N A11') * A12
0.0097557 | -0.00071084 | 0 | -0.00025682 | 0
-0.00071084 | 0.00096766 | -0.00025682 | 0 | 0
0 | -0.00025682 | 0.0011824 | -0.00092562 | 0
-0.00025682 | 0 | -0.00092562 | 0.0036717 | -0.0024892
0 | 0 | 0 | -0.0024892 | 0.017136
B= Inversa negativa de A21 / (N A11') * A12
-109.4781 | -89.2694 | -33.3357 | -17.8162 | -2.588
-89.2694 | -1188.553 | -337.4387 | -101.2867 | -14.7132
-33.3357 | -337.4387 | -1179.1386 | -332.3175 | -48.2735
-17.8162 | -101.2867 | -332.3175 | -396.4197 | -57.5852
-2.588 | -14.7132 | -48.2735 | -57.5852 | -66.7221
A11 * Q |  | A10 * H0 |  | S= A11 Q + A10 H0
5.6896 |  | -100 |  | -94.3104
70.3394 |  | 0 |  | 70.3394
194.6862 |  | 0 |  | 194.6862
54.018 |  | 0 |  | 54.018
194.6862 |  | 0 |  | 194.6862
20.0867 |  | 0 |  | 20.0867
3.4137 |  | -100 |  | -96.5863
M * S |  | A21 * Q |  | C = (M * S) (A21 *Q - q)
-0.9288 |  | -0.1 |  | -0.7688
0.1 |  | 0.2 |  | -0.06
0 |  | 0 |  | 0.03
0.05 |  | 0.1 |  | -0.02
-1.4647 |  | 0 |  | -1.4247
H i+1 = B * C
92.5663
152.8076
85.9207
99.7729
97.6327
A12 H |  | T= A12 H + A10 H0 |  | W= R * T
92.5663 |  | -7.4337 |  | -0.065327
60.2413 |  | 60.2413 |  | 0.042822
66.8869 |  | 66.8869 |  | 0.017178
-13.8522 |  | -13.8522 |  | -0.012822
7.2066 |  | 7.2066 |  | 0.0018508
2.1402 |  | 2.1402 |  | 0.0053273
97.6327 |  | -2.3673 |  | -0.034673
Y= R * A11
0.5 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0.5 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0.5 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0.5 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0.5 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0.5 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0.5
L= I-Y
0.5 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0.5 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0.5 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0.5 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0.5 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0.5 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0.5
X = L * A11 Q |  | Qi+1
0.05 |  | 0.11533
0.05 |  | 0.0071781
0.05 |  | 0.032822
0.05 |  | 0.062822
0.05 |  | 0.048149
0.05 |  | 0.044673
0.05 |  | 0.084673

## I2
Iteración 2
Tramo | D | L | ks | km | A
1-2 | 0.25 | 500 | 6e-05 | 0 | 0.049087
2-3 | 0.15 | 400 | 6e-05 | 10 | 0.017671
3-4 | 0.1 | 200 | 6e-05 | 0 | 0.007854
4-5 | 0.15 | 400 | 6e-05 | 0 | 0.017671
2-5 | 0.1 | 200 | 6e-05 | 0 | 0.007854
5-6 | 0.2 | 600 | 6e-05 | 0 | 0.031416
1-6 | 0.25 | 300 | 6e-05 | 0 | 0.049087
A12 Topología de la red (tramos) | [7 empty] | A10 Nodos con carga fija |  |  | N coeficiente de pérdidas
NT / NN | 1 | 2 | 3 | 4 | 5 | 6 |  | NT | NUDO | CARGA
1 | -1 | 1 | 0 | 0 | 0 | 0 |  | 1 | -1 | 100 | 2 | 0 | 0 | 0 | 0 | 0 | 0
2 |  | -1 | 1 | 0 | 0 | 0 |  | 2 | 0 |  | 0 | 2 | 0 | 0 | 0 | 0 | 0
3 |  | 0 | 1 | -1 | 0 | 0 |  | 3 | 0 |  | 0 | 0 | 2 | 0 | 0 | 0 | 0
4 |  | 0 | 0 | 1 | -1 | 0 |  | 4 | 0 |  | 0 | 0 | 0 | 2 | 0 | 0 | 0
5 |  | -1 | 0 | 0 | 1 | 0 |  | 5 | 0 |  | 0 | 0 | 0 | 0 | 2 | 0 | 0
6 |  | 0 | 0 | 0 | 1 | -1 |  | 6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 2 | 0
7 | -1 | 0 | 0 | 0 | 0 | 1 |  | 1 | -1 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 2
A21 Transpuesta de A12 | [7 empty] | q Consumos |  |  | Matriz identidad
1 | -1 | 0 | 0 | -1 | 0 | 0 |  | 2 | 0.06 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
0 | 1 | 1 | 0 | 0 | 0 | 0 |  | 3 | 0.04 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0
0 | 0 | -1 | 1 | 0 | 0 | 0 |  | 4 | 0.03 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0
0 | 0 | 0 | -1 | 1 | 1 | 0 |  | 5 | 0.03 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | -1 | 1 |  | 6 | 0.04 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1
Tubería | Q | v | Re | f | hf | hm | hf+hm | alpha
1-2 | 0.11533 | 2.3494 | 515225.6294 | 0.015837 | 8.9109 | 0 | 8.9109 | 669.9704
2-3 | 0.0071781 | 0.4062 | 53447.3163 | 0.02202 | 0.49382 | 0.084097 | 0.57791 | 11216.017
3-4 | 0.032822 | 4.179 | 366579.7431 | 0.018658 | 33.216 | 0 | 33.216 | 30833.3656
4-5 | 0.062822 | 3.555 | 467761.8541 | 0.017184 | 29.5173 | 0 | 29.5173 | 7479.1973
2-5 | 0.048149 | 6.1305 | 537767.0229 | 0.018317 | 70.1735 | 0 | 70.1735 | 30268.7958
5-6 | 0.044673 | 1.422 | 249469.3982 | 0.017371 | 5.3706 | 0 | 5.3706 | 2691.1464
1-6 | 0.084673 | 1.7249 | 378275.8055 | 0.016253 | 2.9577 | 0 | 2.9577 | 412.5441
A11
77.2659 | 0 | 0 | 0 | 0 | 0 | 0
0 | 80.5101 | 0 | 0 | 0 | 0 | 0
0 | 0 | 1012.0084 | 0 | 0 | 0 | 0
0 | 0 | 0 | 469.8571 | 0 | 0 | 0
0 | 0 | 0 | 0 | 1457.4177 | 0 | 0
0 | 0 | 0 | 0 | 0 | 120.2207 | 0
0 | 0 | 0 | 0 | 0 | 0 | 34.9312
A11'
77.2659 | 0 | 0 | 0 | 0 | 0 | 0
0 | 80.5101 | 0 | 0 | 0 | 0 | 0
0 | 0 | 1012.0084 | 0 | 0 | 0 | 0
0 | 0 | 0 | 469.8571 | 0 | 0 | 0
0 | 0 | 0 | 0 | 1457.4177 | 0 | 0
0 | 0 | 0 | 0 | 0 | 120.2207 | 0
0 | 0 | 0 | 0 | 0 | 0 | 34.9312
N * A11'
154.5318 | 0 | 0 | 0 | 0 | 0 | 0
0 | 161.0203 | 0 | 0 | 0 | 0 | 0
0 | 0 | 2024.0168 | 0 | 0 | 0 | 0
0 | 0 | 0 | 939.7142 | 0 | 0 | 0
0 | 0 | 0 | 0 | 2914.8354 | 0 | 0
0 | 0 | 0 | 0 | 0 | 240.4414 | 0
0 | 0 | 0 | 0 | 0 | 0 | 69.8624
R = inversa de (N * A11')
0.0064712 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0.0062104 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0.00049407 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0.0010642 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0.00034307 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0.004159 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0.014314
M= A21 / (N A11')
0.0064712 | -0.0062104 | 0 | 0 | -0.00034307 | 0 | 0
0 | 0.0062104 | 0.00049407 | 0 | 0 | 0 | 0
0 | 0 | -0.00049407 | 0.0010642 | 0 | 0 | 0
0 | 0 | 0 | -0.0010642 | 0.00034307 | 0.004159 | 0
0 | 0 | 0 | 0 | 0 | -0.004159 | 0.014314
C =A21 / (N A11') * A12
0.013025 | -0.0062104 | 0 | -0.00034307 | 0
-0.0062104 | 0.0067045 | -0.00049407 | 0 | 0
0 | -0.00049407 | 0.0015582 | -0.0010642 | 0
-0.00034307 | 0 | -0.0010642 | 0.0055662 | -0.004159
0 | 0 | 0 | -0.004159 | 0.018473
B= Inversa negativa de A21 / (N A11') * A12
-142.4278 | -136.3409 | -59.8285 | -24.3051 | -5.4721
-136.3409 | -283.9202 | -114.9689 | -36.5279 | -8.224
-59.8285 | -114.9689 | -808.0814 | -190.1668 | -42.8145
-24.3051 | -36.5279 | -190.1668 | -261.4985 | -58.8743
-5.4721 | -8.224 | -42.8145 | -58.8743 | -67.3885
A11 * Q |  | A10 * H0 |  | S= A11 Q + A10 H0
8.9109 |  | -100 |  | -91.0891
0.57791 |  | 0 |  | 0.57791
33.216 |  | 0 |  | 33.216
29.5173 |  | 0 |  | 29.5173
70.1735 |  | 0 |  | 70.1735
5.3706 |  | 0 |  | 5.3706
2.9577 |  | -100 |  | -97.0423
M * S |  | A21 * Q |  | C = (M * S) (A21 *Q - q)
-0.61712 |  | 0.06 |  | -0.61712
0.02 |  | 0.04 |  | 0.02
0.015 |  | 0.03 |  | 0.015
0.015 |  | 0.03 |  | 0.015
-1.4114 |  | 0.04 |  | -1.4114
H i+1 = B * C
91.6289
87.7944
80.0758
90.5878
96.7983
A12 H |  | T= A12 H + A10 H0 |  | W= R * T
91.6289 |  | -8.3711 |  | -0.054171
-3.8345 |  | -3.8345 |  | -0.023814
7.7187 |  | 7.7187 |  | 0.0038135
-10.5121 |  | -10.5121 |  | -0.011186
-1.0411 |  | -1.0411 |  | -0.00035717
-6.2104 |  | -6.2104 |  | -0.025829
96.7983 |  | -3.2017 |  | -0.045829
Y= R * A11
0.5 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0.5 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0.5 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0.5 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0.5 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0.5 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0.5
L= I-Y
0.5 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0.5 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0.5 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0.5 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0.5 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0.5 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0.5
X = L * A11 Q |  | Qi+1 |  | dq= Qi+1 – Qi
0.057664 |  | 0.11183 |  | -0.0034929
0.0035891 |  | 0.027403 |  | 0.020224
0.016411 |  | 0.012597 |  | -0.020224
0.031411 |  | 0.042597 |  | -0.020224
0.024075 |  | 0.024432 |  | -0.023717
0.022336 |  | 0.048166 |  | 0.0034929
0.042336 |  | 0.088166 |  | 0.0034929

## I3
Iteración 3
Tramo | D | L | ks | km | A
1-2 | 0.25 | 500 | 1.5e-06 | 0 | 0.049087
2-3 | 0.15 | 400 | 1.5e-06 | 10 | 0.017671
3-4 | 0.1 | 200 | 1.5e-06 | 0 | 0.007854
4-5 | 0.15 | 400 | 1.5e-06 | 0 | 0.017671
2-5 | 0.1 | 200 | 1.5e-06 | 0 | 0.007854
5-6 | 0.2 | 600 | 1.5e-06 | 0 | 0.031416
1-6 | 0.25 | 300 | 1.5e-06 | 0 | 0.049087
A12 Topología de la red (tramos) | [7 empty] | A10 Nodos con carga fija |  |  | N coeficiente de pérdidas
NT / NN | 1 | 2 | 3 | 4 | 5 | 6 |  | NT | NUDO | CARGA
1 | -1 | 1 | 0 | 0 | 0 | 0 |  | 1 | -1 | 100 | 2 | 0 | 0 | 0 | 0 | 0 | 0
2 |  | -1 | 1 | 0 | 0 | 0 |  | 2 | 0 |  | 0 | 2 | 0 | 0 | 0 | 0 | 0
3 |  | 0 | 1 | -1 | 0 | 0 |  | 3 | 0 |  | 0 | 0 | 2 | 0 | 0 | 0 | 0
4 |  | 0 | 0 | 1 | -1 | 0 |  | 4 | 0 |  | 0 | 0 | 0 | 2 | 0 | 0 | 0
5 |  | -1 | 0 | 0 | 1 | 0 |  | 5 | 0 |  | 0 | 0 | 0 | 0 | 2 | 0 | 0
6 |  | 0 | 0 | 0 | 1 | -1 |  | 6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 2 | 0
7 | -1 | 0 | 0 | 0 | 0 | 1 |  | 1 | -1 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 2
A21 Transpuesta de A12 | [7 empty] | q Consumos |  |  | Matriz identidad
1 | -1 | 0 | 0 | -1 | 0 | 0 |  | 2 | 0.06 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
0 | 1 | 1 | 0 | 0 | 0 | 0 |  | 3 | 0.04 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0
0 | 0 | -1 | 1 | 0 | 0 | 0 |  | 4 | 0.03 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0
0 | 0 | 0 | -1 | 1 | 1 | 0 |  | 5 | 0.03 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | -1 | 1 |  | 6 | 0.04 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1
Tubería | Q | v | Re | f | hf | hm | hf+hm | alpha
1-2 | 0.11183 | 2.2783 | 499620.8653 | 0.01319 | 6.9787 | 0 | 6.9787 | 557.983
2-3 | 0.027403 | 1.5507 | 204035.6481 | 0.015565 | 5.0869 | 1.2256 | 6.3125 | 8406.5652
3-4 | 0.012597 | 1.6039 | 140697.2453 | 0.016765 | 4.3967 | 0 | 4.3967 | 27705.5905
4-5 | 0.042597 | 2.4105 | 317173.5223 | 0.014347 | 11.3306 | 0 | 11.3306 | 6244.3343
2-5 | 0.024432 | 3.1107 | 272872.6149 | 0.014799 | 14.5977 | 0 | 14.5977 | 24455.481
5-6 | 0.048166 | 1.5332 | 268975.3533 | 0.014755 | 5.3033 | 0 | 5.3033 | 2285.997
1-6 | 0.088166 | 1.7961 | 393880.5696 | 0.013751 | 2.7132 | 0 | 2.7132 | 349.0522
A11
62.4017 | 0 | 0 | 0 | 0 | 0 | 0
0 | 230.3619 | 0 | 0 | 0 | 0 | 0
0 | 0 | 349.0179 | 0 | 0 | 0 | 0
0 | 0 | 0 | 265.9923 | 0 | 0 | 0
0 | 0 | 0 | 0 | 597.4903 | 0 | 0
0 | 0 | 0 | 0 | 0 | 110.1065 | 0
0 | 0 | 0 | 0 | 0 | 0 | 30.7744
A11'
62.4017 | 0 | 0 | 0 | 0 | 0 | 0
0 | 230.3619 | 0 | 0 | 0 | 0 | 0
0 | 0 | 349.0179 | 0 | 0 | 0 | 0
0 | 0 | 0 | 265.9923 | 0 | 0 | 0
0 | 0 | 0 | 0 | 597.4903 | 0 | 0
0 | 0 | 0 | 0 | 0 | 110.1065 | 0
0 | 0 | 0 | 0 | 0 | 0 | 30.7744
N * A11'
124.8034 | 0 | 0 | 0 | 0 | 0 | 0
0 | 460.7238 | 0 | 0 | 0 | 0 | 0
0 | 0 | 698.0359 | 0 | 0 | 0 | 0
0 | 0 | 0 | 531.9846 | 0 | 0 | 0
0 | 0 | 0 | 0 | 1194.9807 | 0 | 0
0 | 0 | 0 | 0 | 0 | 220.213 | 0
0 | 0 | 0 | 0 | 0 | 0 | 61.5488
R = inversa de (N * A11')
0.0080126 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0.0021705 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0.0014326 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0.0018798 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0.00083683 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0.0045411 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0.016247
M= A21 / (N A11')
0.0080126 | -0.0021705 | 0 | 0 | -0.00083683 | 0 | 0
0 | 0.0021705 | 0.0014326 | 0 | 0 | 0 | 0
0 | 0 | -0.0014326 | 0.0018798 | 0 | 0 | 0
0 | 0 | 0 | -0.0018798 | 0.00083683 | 0.0045411 | 0
0 | 0 | 0 | 0 | 0 | -0.0045411 | 0.016247
C =A21 / (N A11') * A12
0.01102 | -0.0021705 | 0 | -0.00083683 | 0
-0.0021705 | 0.0036031 | -0.0014326 | 0 | 0
0 | -0.0014326 | 0.0033123 | -0.0018798 | 0
-0.00083683 | 0 | -0.0018798 | 0.0072576 | -0.0045411
0 | 0 | 0 | -0.0045411 | 0.020788
B= Inversa negativa de A21 / (N A11') * A12
-110.7292 | -89.2142 | -56.6171 | -31.7744 | -6.9409
-89.2142 | -421.9757 | -228.102 | -80.3477 | -17.5514
-56.6171 | -228.102 | -487.9162 | -153.9403 | -33.6271
-31.7744 | -80.3477 | -153.9403 | -210.0265 | -45.8788
-6.9409 | -17.5514 | -33.6271 | -45.8788 | -58.1258
A11 * Q |  | A10 * H0 |  | S= A11 Q + A10 H0
6.9787 |  | -100 |  | -93.0213
6.3125 |  | 0 |  | 6.3125
4.3967 |  | 0 |  | 4.3967
11.3306 |  | 0 |  | 11.3306
14.5977 |  | 0 |  | 14.5977
5.3033 |  | 0 |  | 5.3033
2.7132 |  | -100 |  | -97.2868
M * S |  | A21 * Q |  | C = (M * S) (A21 *Q - q)
-0.77126 |  | 0.06 |  | -0.77126
0.02 |  | 0.04 |  | 0.02
0.015 |  | 0.03 |  | 0.015
0.015 |  | 0.03 |  | 0.015
-1.6047 |  | 0.04 |  | -1.6047
H i+1 = B * C
93.4291
83.9063
83.4391
91.0627
97.0856
A12 H |  | T= A12 H + A10 H0 |  | W= R * T
93.4291 |  | -6.5709 |  | -0.05265
-9.5229 |  | -9.5229 |  | -0.020669
0.46723 |  | 0.46723 |  | 0.00066935
-7.6237 |  | -7.6237 |  | -0.014331
-2.3664 |  | -2.3664 |  | -0.0019803
-6.0229 |  | -6.0229 |  | -0.02735
97.0856 |  | -2.9144 |  | -0.04735
Y= R * A11
0.5 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0.5 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0.5 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0.5 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0.5 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0.5 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0.5
L= I-Y
0.5 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0.5 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0.5 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0.5 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0.5 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0.5 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0.5
dq= L * A11 Q |  | Qi+1 |  | dq=Qi+1 – Qi
0.055917 |  | 0.10857 |  | -0.0032675
0.013701 |  | 0.034371 |  | 0.006968
0.0062987 |  | 0.0056293 |  | -0.006968
0.021299 |  | 0.035629 |  | -0.006968
0.012216 |  | 0.014196 |  | -0.010236
0.024083 |  | 0.051433 |  | 0.0032675
0.044083 |  | 0.091433 |  | 0.0032675

## I4
Iteración 4
Tramo | D | L | ks | km | A
1-2 | 0.25 | 500 | 1.5e-06 | 0 | 0.049087
2-3 | 0.15 | 400 | 1.5e-06 | 10 | 0.017671
3-4 | 0.1 | 200 | 1.5e-06 | 0 | 0.007854
4-5 | 0.15 | 400 | 1.5e-06 | 0 | 0.017671
2-5 | 0.1 | 200 | 1.5e-06 | 0 | 0.007854
5-6 | 0.2 | 600 | 1.5e-06 | 0 | 0.031416
1-6 | 0.25 | 300 | 1.5e-06 | 0 | 0.049087
A12 Topología de la red (tramos) | [7 empty] | A10 Nodos con carga fija |  |  | N coeficiente de pérdidas
NT / NN | 1 | 2 | 3 | 4 | 5 | 6 |  | NT | NUDO | CARGA
1 | -1 | 1 | 0 | 0 | 0 | 0 |  | 1 | -1 | 100 | 2 | 0 | 0 | 0 | 0 | 0 | 0
2 |  | -1 | 1 | 0 | 0 | 0 |  | 2 | 0 |  | 0 | 2 | 0 | 0 | 0 | 0 | 0
3 |  | 0 | 1 | -1 | 0 | 0 |  | 3 | 0 |  | 0 | 0 | 2 | 0 | 0 | 0 | 0
4 |  | 0 | 0 | 1 | -1 | 0 |  | 4 | 0 |  | 0 | 0 | 0 | 2 | 0 | 0 | 0
5 |  | -1 | 0 | 0 | 1 | 0 |  | 5 | 0 |  | 0 | 0 | 0 | 0 | 2 | 0 | 0
6 |  | 0 | 0 | 0 | 1 | -1 |  | 6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 2 | 0
7 | -1 | 0 | 0 | 0 | 0 | 1 |  | 1 | -1 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 2
A21 Transpuesta de A12 | [7 empty] | q Consumos |  |  | Matriz identidad
1 | -1 | 0 | 0 | -1 | 0 | 0 |  | 2 | 0.06 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
0 | 1 | 1 | 0 | 0 | 0 | 0 |  | 3 | 0.04 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0
0 | 0 | -1 | 1 | 0 | 0 | 0 |  | 4 | 0.03 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0
0 | 0 | 0 | -1 | 1 | 1 | 0 |  | 5 | 0.03 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | -1 | 1 |  | 6 | 0.04 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1
Tubería | Q | v | Re | f | hf | hm | hf+hm | alpha
1-2 | 0.10857 | 2.2117 | 485023.0901 | 0.013257 | 6.6107 | 0 | 6.6107 | 560.8576
2-3 | 0.034371 | 1.945 | 255918.6208 | 0.014919 | 7.6707 | 1.9281 | 9.5988 | 8125.3597
3-4 | 0.0056293 | 0.71675 | 62872.7863 | 0.0198 | 1.0369 | 0 | 1.0369 | 32719.9113
4-5 | 0.035629 | 2.0162 | 265290.5496 | 0.01482 | 8.1884 | 0 | 8.1884 | 6450.3591
2-5 | 0.014196 | 1.8075 | 158553.718 | 0.016379 | 5.4549 | 0 | 5.4549 | 27067.5017
5-6 | 0.051433 | 1.6372 | 287222.5722 | 0.014578 | 5.9746 | 0 | 5.9746 | 2258.5275
1-6 | 0.091433 | 1.8627 | 408478.3448 | 0.013663 | 2.8993 | 0 | 2.8993 | 346.8047
A11
60.8905 | 0 | 0 | 0 | 0 | 0 | 0
0 | 279.274 | 0 | 0 | 0 | 0 | 0
0 | 0 | 184.1915 | 0 | 0 | 0 | 0
0 | 0 | 0 | 229.822 | 0 | 0 | 0
0 | 0 | 0 | 0 | 384.2548 | 0 | 0
0 | 0 | 0 | 0 | 0 | 116.1632 | 0
0 | 0 | 0 | 0 | 0 | 0 | 31.7095
A11'
60.8905 | 0 | 0 | 0 | 0 | 0 | 0
0 | 279.274 | 0 | 0 | 0 | 0 | 0
0 | 0 | 184.1915 | 0 | 0 | 0 | 0
0 | 0 | 0 | 229.822 | 0 | 0 | 0
0 | 0 | 0 | 0 | 384.2548 | 0 | 0
0 | 0 | 0 | 0 | 0 | 116.1632 | 0
0 | 0 | 0 | 0 | 0 | 0 | 31.7095
N * A11'
121.7811 | 0 | 0 | 0 | 0 | 0 | 0
0 | 558.548 | 0 | 0 | 0 | 0 | 0
0 | 0 | 368.383 | 0 | 0 | 0 | 0
0 | 0 | 0 | 459.6441 | 0 | 0 | 0
0 | 0 | 0 | 0 | 768.5097 | 0 | 0
0 | 0 | 0 | 0 | 0 | 232.3265 | 0
0 | 0 | 0 | 0 | 0 | 0 | 63.4189
R = inversa de (N * A11')
0.0082115 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0.0017904 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0.0027146 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0.0021756 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0.0013012 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0.0043043 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0.015768
M= A21 / (N A11')
0.0082115 | -0.0017904 | 0 | 0 | -0.0013012 | 0 | 0
0 | 0.0017904 | 0.0027146 | 0 | 0 | 0 | 0
0 | 0 | -0.0027146 | 0.0021756 | 0 | 0 | 0
0 | 0 | 0 | -0.0021756 | 0.0013012 | 0.0043043 | 0
0 | 0 | 0 | 0 | 0 | -0.0043043 | 0.015768
C =A21 / (N A11') * A12
0.011303 | -0.0017904 | 0 | -0.0013012 | 0
-0.0017904 | 0.0045049 | -0.0027146 | 0 | 0
0 | -0.0027146 | 0.0048902 | -0.0021756 | 0
-0.0013012 | 0 | -0.0021756 | 0.0077811 | -0.0043043
0 | 0 | 0 | -0.0043043 | 0.020072
B= Inversa negativa de A21 / (N A11') * A12
-105.5191 | -78.9218 | -61.3798 | -39.4922 | -8.4686
-78.9218 | -422.6082 | -280.8991 | -104.0838 | -22.3195
-61.3798 | -280.8991 | -425.6802 | -146.6844 | -31.4546
-39.4922 | -104.0838 | -146.6844 | -199.8386 | -42.8529
-8.4686 | -22.3195 | -31.4546 | -42.8529 | -59.0088
A11 * Q |  | A10 * H0 |  | S= A11 Q + A10 H0
6.6107 |  | -100 |  | -93.3893
9.5988 |  | 0 |  | 9.5988
1.0369 |  | 0 |  | 1.0369
8.1884 |  | 0 |  | 8.1884
5.4549 |  | 0 |  | 5.4549
5.9746 |  | 0 |  | 5.9746
2.8993 |  | -100 |  | -97.1007
M * S |  | A21 * Q |  | C = (M * S) (A21 *Q - q)
-0.79115 |  | 0.06 |  | -0.79115
0.02 |  | 0.04 |  | 0.02
0.015 |  | 0.03 |  | 0.015
0.015 |  | 0.03 |  | 0.015
-1.5568 |  | 0.04 |  | -1.5568
H i+1 = B * C
93.5735
82.959
83.3261
90.6787
97.0048
A12 H |  | T= A12 H + A10 H0 |  | W= R * T
93.5735 |  | -6.4265 |  | -0.052771
-10.6145 |  | -10.6145 |  | -0.019004
-0.36701 |  | -0.36701 |  | -0.00099628
-7.3526 |  | -7.3526 |  | -0.015996
-2.8949 |  | -2.8949 |  | -0.0037669
-6.3261 |  | -6.3261 |  | -0.027229
97.0048 |  | -2.9952 |  | -0.047229
Y= R * A11
0.5 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0.5 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0.5 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0.5 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0.5 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0.5 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0.5
L= I-Y
0.5 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0.5 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0.5 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0.5 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0.5 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0.5 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0.5
dq= L * A11 Q |  | Qi+1 |  | dq=Qi+1 – Qi
0.054283 |  | 0.10705 |  | -0.0015128
0.017185 |  | 0.036189 |  | 0.0018184
0.0028147 |  | 0.0038109 |  | -0.0018184
0.017815 |  | 0.033811 |  | -0.0018184
0.0070981 |  | 0.010865 |  | -0.0033312
0.025717 |  | 0.052946 |  | 0.0015128
0.045717 |  | 0.092946 |  | 0.0015128

## I5
Iteración 5
Tramo | D | L | ks | km | A
1-2 | 0.25 | 500 | 1.5e-06 | 0 | 0.049087
2-3 | 0.15 | 400 | 1.5e-06 | 10 | 0.017671
3-4 | 0.1 | 200 | 1.5e-06 | 0 | 0.007854
4-5 | 0.15 | 400 | 1.5e-06 | 0 | 0.017671
2-5 | 0.1 | 200 | 1.5e-06 | 0 | 0.007854
5-6 | 0.2 | 600 | 1.5e-06 | 0 | 0.031416
1-6 | 0.25 | 300 | 1.5e-06 | 0 | 0.049087
A12 Topología de la red (tramos) | [7 empty] | A10 Nodos con carga fija |  |  | N coeficiente de pérdidas
NT / NN | 1 | 2 | 3 | 4 | 5 | 6 |  | NT | NUDO | CARGA
1 | -1 | 1 | 0 | 0 | 0 | 0 |  | 1 | -1 | 100 | 2 | 0 | 0 | 0 | 0 | 0 | 0
2 |  | -1 | 1 | 0 | 0 | 0 |  | 2 | 0 |  | 0 | 2 | 0 | 0 | 0 | 0 | 0
3 |  | 0 | 1 | -1 | 0 | 0 |  | 3 | 0 |  | 0 | 0 | 2 | 0 | 0 | 0 | 0
4 |  | 0 | 0 | 1 | -1 | 0 |  | 4 | 0 |  | 0 | 0 | 0 | 2 | 0 | 0 | 0
5 |  | -1 | 0 | 0 | 1 | 0 |  | 5 | 0 |  | 0 | 0 | 0 | 0 | 2 | 0 | 0
6 |  | 0 | 0 | 0 | 1 | -1 |  | 6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 2 | 0
7 | -1 | 0 | 0 | 0 | 0 | 1 |  | 1 | -1 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 2
A21 Transpuesta de A12 | [7 empty] | q Consumos |  |  | Matriz identidad
1 | -1 | 0 | 0 | -1 | 0 | 0 |  | 2 | 0.06 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
0 | 1 | 1 | 0 | 0 | 0 | 0 |  | 3 | 0.04 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0
0 | 0 | -1 | 1 | 0 | 0 | 0 |  | 4 | 0.03 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0
0 | 0 | 0 | -1 | 1 | 1 | 0 |  | 5 | 0.03 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | -1 | 1 |  | 6 | 0.04 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1
Tubería | Q | v | Re | f | hf | hm | hf+hm | alpha
1-2 | 0.10705 | 2.1809 | 478264.6011 | 0.01329 | 6.4434 | 0 | 6.4434 | 562.2266
2-3 | 0.036189 | 2.0479 | 269458.0909 | 0.014778 | 8.4236 | 2.1375 | 10.5611 | 8064.0638
3-4 | 0.0038109 | 0.48522 | 42563.5811 | 0.021591 | 0.5182 | 0 | 0.5182 | 35680.5424
4-5 | 0.033811 | 1.9133 | 251751.0795 | 0.014964 | 7.4455 | 0 | 7.4455 | 6512.9503
2-5 | 0.010865 | 1.3834 | 121348.2902 | 0.017265 | 3.3679 | 0 | 3.3679 | 28530.4029
5-6 | 0.052946 | 1.6853 | 295670.6836 | 0.014501 | 6.2977 | 0 | 6.2977 | 2246.567
1-6 | 0.091433 | 1.8627 | 408478.3448 | 0.013663 | 2.8993 | 0 | 2.8993 | 346.8047
A11
60.1886 | 0 | 0 | 0 | 0 | 0 | 0
0 | 291.8308 | 0 | 0 | 0 | 0 | 0
0 | 0 | 135.9767 | 0 | 0 | 0 | 0
0 | 0 | 0 | 220.209 | 0 | 0 | 0
0 | 0 | 0 | 0 | 309.9819 | 0 | 0
0 | 0 | 0 | 0 | 0 | 118.9467 | 0
0 | 0 | 0 | 0 | 0 | 0 | 31.7095
A11'
60.1886 | 0 | 0 | 0 | 0 | 0 | 0
0 | 291.8308 | 0 | 0 | 0 | 0 | 0
0 | 0 | 135.9767 | 0 | 0 | 0 | 0
0 | 0 | 0 | 220.209 | 0 | 0 | 0
0 | 0 | 0 | 0 | 309.9819 | 0 | 0
0 | 0 | 0 | 0 | 0 | 118.9467 | 0
0 | 0 | 0 | 0 | 0 | 0 | 31.7095
N * A11'
120.3772 | 0 | 0 | 0 | 0 | 0 | 0
0 | 583.6617 | 0 | 0 | 0 | 0 | 0
0 | 0 | 271.9533 | 0 | 0 | 0 | 0
0 | 0 | 0 | 440.418 | 0 | 0 | 0
0 | 0 | 0 | 0 | 619.9637 | 0 | 0
0 | 0 | 0 | 0 | 0 | 237.8934 | 0
0 | 0 | 0 | 0 | 0 | 0 | 63.4189
R = inversa de (N * A11')
0.0083072 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0.0017133 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0.0036771 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0.0022706 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0.001613 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0.0042036 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0.015768
M= A21 / (N A11')
0.0083072 | -0.0017133 | 0 | 0 | -0.001613 | 0 | 0
0 | 0.0017133 | 0.0036771 | 0 | 0 | 0 | 0
0 | 0 | -0.0036771 | 0.0022706 | 0 | 0 | 0
0 | 0 | 0 | -0.0022706 | 0.001613 | 0.0042036 | 0
0 | 0 | 0 | 0 | 0 | -0.0042036 | 0.015768
C =A21 / (N A11') * A12
0.011634 | -0.0017133 | 0 | -0.001613 | 0
-0.0017133 | 0.0053904 | -0.0036771 | 0 | 0
0 | -0.0036771 | 0.0059477 | -0.0022706 | 0
-0.001613 | 0 | -0.0022706 | 0.0080871 | -0.0042036
0 | 0 | 0 | -0.0042036 | 0.019972
B= Inversa negativa de A21 / (N A11') * A12
-103.148 | -76.1174 | -63.5227 | -43.126 | -9.077
-76.1174 | -412.5426 | -297.3444 | -110.7853 | -23.3176
-63.5227 | -297.3444 | -406.2921 | -142.3108 | -29.953
-43.126 | -110.7853 | -142.3108 | -193.365 | -40.6986
-9.077 | -23.3176 | -29.953 | -40.6986 | -58.6368
A11 * Q |  | A10 * H0 |  | S= A11 Q + A10 H0
6.4434 |  | -100 |  | -93.5566
10.5611 |  | 0 |  | 10.5611
0.5182 |  | 0 |  | 0.5182
7.4455 |  | 0 |  | 7.4455
3.3679 |  | 0 |  | 3.3679
6.2977 |  | 0 |  | 6.2977
2.8993 |  | -100 |  | -97.1007
M * S |  | A21 * Q |  | C = (M * S) (A21 *Q - q)
-0.80072 |  | 0.06 |  | -0.80072
0.02 |  | 0.04 |  | 0.02
0.015 |  | 0.03 |  | 0.015
0.015 |  | 0.03 |  | 0.015
-1.5576 |  | 0.038487 |  | -1.5561
H i+1 = B * C
93.5951
82.8597
83.2967
90.6106
96.9845
A12 H |  | T= A12 H + A10 H0 |  | W= R * T
93.5951 |  | -6.4049 |  | -0.053207
-10.7354 |  | -10.7354 |  | -0.018393
-0.43698 |  | -0.43698 |  | -0.0016068
-7.3139 |  | -7.3139 |  | -0.016607
-2.9845 |  | -2.9845 |  | -0.0048139
-6.3739 |  | -6.3739 |  | -0.026793
96.9845 |  | -3.0155 |  | -0.047549
Y= R * A11
0.5 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0.5 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0.5 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0.5 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0.5 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0.5 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0.5
L= I-Y
0.5 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0.5 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0.5 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0.5 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0.5 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0.5 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0.5
dq= L * A11 Q |  | Qi+1 |  | dq=Qi+1 – Qi
0.053527 |  | 0.10673 |  | -0.00031992
0.018095 |  | 0.036488 |  | 0.00029864
0.0019055 |  | 0.0035123 |  | -0.00029864
0.016905 |  | 0.033512 |  | -0.00029864
0.0054325 |  | 0.010246 |  | -0.00061856
0.026473 |  | 0.053266 |  | 0.00031992
0.045717 |  | 0.093266 |  | 0.00031992

## I6
Iteración 6
Tramo | D | L | ks | km | A
1-2 | 0.25 | 500 | 1.5e-06 | 0 | 0.049087
2-3 | 0.15 | 400 | 1.5e-06 | 10 | 0.017671
3-4 | 0.1 | 200 | 1.5e-06 | 0 | 0.007854
4-5 | 0.15 | 400 | 1.5e-06 | 0 | 0.017671
2-5 | 0.1 | 200 | 1.5e-06 | 0 | 0.007854
5-6 | 0.2 | 600 | 1.5e-06 | 0 | 0.031416
1-6 | 0.25 | 300 | 1.5e-06 | 0 | 0.049087
A12 Topología de la red (tramos) | [7 empty] | A10 Nodos con carga fija |  |  | N coeficiente de pérdidas
NT / NN | 1 | 2 | 3 | 4 | 5 | 6 |  | NT | NUDO | CARGA
1 | -1 | 1 | 0 | 0 | 0 | 0 |  | 1 | -1 | 100 | 2 | 0 | 0 | 0 | 0 | 0 | 0
2 |  | -1 | 1 | 0 | 0 | 0 |  | 2 | 0 |  | 0 | 2 | 0 | 0 | 0 | 0 | 0
3 |  | 0 | 1 | -1 | 0 | 0 |  | 3 | 0 |  | 0 | 0 | 2 | 0 | 0 | 0 | 0
4 |  | 0 | 0 | 1 | -1 | 0 |  | 4 | 0 |  | 0 | 0 | 0 | 2 | 0 | 0 | 0
5 |  | -1 | 0 | 0 | 1 | 0 |  | 5 | 0 |  | 0 | 0 | 0 | 0 | 2 | 0 | 0
6 |  | 0 | 0 | 0 | 1 | -1 |  | 6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 2 | 0
7 | -1 | 0 | 0 | 0 | 0 | 1 |  | 1 | -1 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 2
A21 Transpuesta de A12 | [7 empty] | q Consumos |  |  | Matriz identidad
1 | -1 | 0 | 0 | -1 | 0 | 0 |  | 2 | 0.06 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
0 | 1 | 1 | 0 | 0 | 0 | 0 |  | 3 | 0.04 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0
0 | 0 | -1 | 1 | 0 | 0 | 0 |  | 4 | 0.03 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0
0 | 0 | 0 | -1 | 1 | 1 | 0 |  | 5 | 0.03 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | -1 | 1 |  | 6 | 0.04 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1
Tubería | Q | v | Re | f | hf | hm | hf+hm | alpha
1-2 | 0.10673 | 2.1744 | 476835.3698 | 0.013297 | 6.4083 | 0 | 6.4083 | 562.5193
2-3 | 0.036488 | 2.0648 | 271681.7418 | 0.014756 | 8.5503 | 2.1729 | 10.7232 | 8054.3815
3-4 | 0.0035123 | 0.4472 | 39228.1048 | 0.021998 | 0.44845 | 0 | 0.44845 | 36352.1924
4-5 | 0.033512 | 1.8964 | 249527.4286 | 0.014989 | 7.3265 | 0 | 7.3265 | 6523.6509
2-5 | 0.010246 | 1.3046 | 114439.7355 | 0.017469 | 3.0308 | 0 | 3.0308 | 28868.2551
5-6 | 0.053266 | 1.6955 | 297457.2227 | 0.014485 | 6.3671 | 0 | 6.3671 | 2244.0946
1-6 | 0.093266 | 1.9 | 416666.0651 | 0.013615 | 3.0061 | 0 | 3.0061 | 345.5891
A11
60.04 | 0 | 0 | 0 | 0 | 0 | 0
0 | 293.8858 | 0 | 0 | 0 | 0 | 0
0 | 0 | 127.6799 | 0 | 0 | 0 | 0
0 | 0 | 0 | 218.6226 | 0 | 0 | 0
0 | 0 | 0 | 0 | 295.7959 | 0 | 0
0 | 0 | 0 | 0 | 0 | 119.5337 | 0
0 | 0 | 0 | 0 | 0 | 0 | 32.2317
A11'
60.04 | 0 | 0 | 0 | 0 | 0 | 0
0 | 293.8858 | 0 | 0 | 0 | 0 | 0
0 | 0 | 127.6799 | 0 | 0 | 0 | 0
0 | 0 | 0 | 218.6226 | 0 | 0 | 0
0 | 0 | 0 | 0 | 295.7959 | 0 | 0
0 | 0 | 0 | 0 | 0 | 119.5337 | 0
0 | 0 | 0 | 0 | 0 | 0 | 32.2317
N * A11'
120.08 | 0 | 0 | 0 | 0 | 0 | 0
0 | 587.7717 | 0 | 0 | 0 | 0 | 0
0 | 0 | 255.3599 | 0 | 0 | 0 | 0
0 | 0 | 0 | 437.2451 | 0 | 0 | 0
0 | 0 | 0 | 0 | 591.5917 | 0 | 0
0 | 0 | 0 | 0 | 0 | 239.0674 | 0
0 | 0 | 0 | 0 | 0 | 0 | 64.4633
R = inversa de (N * A11')
0.0083278 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0.0017013 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0.003916 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0.002287 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0.0016904 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0.0041829 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0.015513
M= A21 / (N A11')
0.0083278 | -0.0017013 | 0 | 0 | -0.0016904 | 0 | 0
0 | 0.0017013 | 0.003916 | 0 | 0 | 0 | 0
0 | 0 | -0.003916 | 0.002287 | 0 | 0 | 0
0 | 0 | 0 | -0.002287 | 0.0016904 | 0.0041829 | 0
0 | 0 | 0 | 0 | 0 | -0.0041829 | 0.015513
C =A21 / (N A11') * A12
0.011719 | -0.0017013 | 0 | -0.0016904 | 0
-0.0017013 | 0.0056174 | -0.003916 | 0 | 0
0 | -0.003916 | 0.0062031 | -0.002287 | 0
-0.0016904 | 0 | -0.002287 | 0.0081603 | -0.0041829
0 | 0 | 0 | -0.0041829 | 0.019696
B= Inversa negativa de A21 / (N A11') * A12
-102.6706 | -75.7401 | -64.04 | -44.0063 | -9.346
-75.7401 | -410.3705 | -300.3922 | -112.0796 | -23.8033
-64.04 | -300.3922 | -403.0764 | -141.6544 | -30.0843
-44.0063 | -112.0796 | -141.6544 | -192.2943 | -40.8391
-9.346 | -23.8033 | -30.0843 | -40.8391 | -59.4461
A11 * Q |  | A10 * H0 |  | S= A11 Q + A10 H0
6.4083 |  | -100 |  | -93.5917
10.7232 |  | 0 |  | 10.7232
0.44845 |  | 0 |  | 0.44845
7.3265 |  | 0 |  | 7.3265
3.0308 |  | 0 |  | 3.0308
6.3671 |  | 0 |  | 6.3671
3.0061 |  | -100 |  | -96.9939
M * S |  | A21 * Q |  | C = (M * S) (A21 *Q - q)
-0.80278 |  | 0.06 |  | -0.80278
0.02 |  | 0.04 |  | 0.02
0.015 |  | 0.03 |  | 0.015
0.015 |  | 0.03 |  | 0.015
-1.5313 |  | 0.04 |  | -1.5313
H i+1 = B * C
93.5975
82.8572
83.2983
90.6122
96.9908
A12 H |  | T= A12 H + A10 H0 |  | W= R * T
93.5975 |  | -6.4025 |  | -0.053319
-10.7402 |  | -10.7402 |  | -0.018273
-0.44106 |  | -0.44106 |  | -0.0017272
-7.3139 |  | -7.3139 |  | -0.016727
-2.9853 |  | -2.9853 |  | -0.0050461
-6.3786 |  | -6.3786 |  | -0.026681
96.9908 |  | -3.0092 |  | -0.046681
Y= R * A11
0.5 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0.5 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0.5 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0.5 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0.5 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0.5 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0.5
L= I-Y
0.5 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0.5 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0.5 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0.5 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0.5 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0.5 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0.5
dq= L * A11 Q |  | Qi+1 |  | dq=Qi+1 – Qi
0.053367 |  | 0.10669 |  | -4.8128e-05
0.018244 |  | 0.036517 |  | 2.8928e-05
0.0017562 |  | 0.0034834 |  | -2.8928e-05
0.016756 |  | 0.033483 |  | -2.8928e-05
0.0051232 |  | 0.010169 |  | -7.7056e-05
0.026633 |  | 0.053314 |  | 4.8128e-05
0.046633 |  | 0.093314 |  | 4.8128e-05

## I7
Iteración 7
Tramo | D | L | ks | km | A
1-2 | 0.25 | 500 | 1.5e-06 | 0 | 0.049087
2-3 | 0.15 | 400 | 1.5e-06 | 10 | 0.017671
3-4 | 0.1 | 200 | 1.5e-06 | 0 | 0.007854
4-5 | 0.15 | 400 | 1.5e-06 | 0 | 0.017671
2-5 | 0.1 | 200 | 1.5e-06 | 0 | 0.007854
5-6 | 0.2 | 600 | 1.5e-06 | 0 | 0.031416
1-6 | 0.25 | 300 | 1.5e-06 | 0 | 0.049087
A12 Topología de la red (tramos) | [7 empty] | A10 Nodos con carga fija |  |  | N coeficiente de pérdidas
NT / NN | 1 | 2 | 3 | 4 | 5 | 6 |  | NT | NUDO | CARGA
1 | -1 | 1 | 0 | 0 | 0 | 0 |  | 1 | -1 | 100 | 2 | 0 | 0 | 0 | 0 | 0 | 0
2 |  | -1 | 1 | 0 | 0 | 0 |  | 2 | 0 |  | 0 | 2 | 0 | 0 | 0 | 0 | 0
3 |  | 0 | 1 | -1 | 0 | 0 |  | 3 | 0 |  | 0 | 0 | 2 | 0 | 0 | 0 | 0
4 |  | 0 | 0 | 1 | -1 | 0 |  | 4 | 0 |  | 0 | 0 | 0 | 2 | 0 | 0 | 0
5 |  | -1 | 0 | 0 | 1 | 0 |  | 5 | 0 |  | 0 | 0 | 0 | 0 | 2 | 0 | 0
6 |  | 0 | 0 | 0 | 1 | -1 |  | 6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 2 | 0
7 | -1 | 0 | 0 | 0 | 0 | 1 |  | 1 | -1 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 2
A21 Transpuesta de A12 | [7 empty] | q Consumos |  |  | Matriz identidad
1 | -1 | 0 | 0 | -1 | 0 | 0 |  | 2 | 0.06 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
0 | 1 | 1 | 0 | 0 | 0 | 0 |  | 3 | 0.04 |  | 0 | 1 | 0 | 0 | 0 | 0 | 0
0 | 0 | -1 | 1 | 0 | 0 | 0 |  | 4 | 0.03 |  | 0 | 0 | 1 | 0 | 0 | 0 | 0
0 | 0 | 0 | -1 | 1 | 1 | 0 |  | 5 | 0.03 |  | 0 | 0 | 0 | 1 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | -1 | 1 |  | 6 | 0.04 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1
Tubería | Q | v | Re | f | hf | hm | hf+hm | alpha
1-2 | 0.10669 | 2.1734 | 476620.3563 | 0.013298 | 6.403 | 0 | 6.403 | 562.5635
2-3 | 0.036517 | 2.0664 | 271897.1352 | 0.014754 | 8.5626 | 2.1764 | 10.739 | 8053.4492
3-4 | 0.0034834 | 0.44352 | 38905.0147 | 0.02204 | 0.44193 | 0 | 0.44193 | 36421.3443
4-5 | 0.033483 | 1.8948 | 249312.0352 | 0.014991 | 7.3151 | 0 | 7.3151 | 6524.694
2-5 | 0.010169 | 1.2948 | 113579.1117 | 0.017496 | 2.99 | 0 | 2.99 | 28912.2328
5-6 | 0.053314 | 1.697 | 297725.9896 | 0.014483 | 6.3775 | 0 | 6.3775 | 2243.7243
1-6 | 0.093314 | 1.901 | 416881.0786 | 0.013614 | 3.0089 | 0 | 3.0089 | 345.5576
A11
60.0176 | 0 | 0 | 0 | 0 | 0 | 0
0 | 294.0848 | 0 | 0 | 0 | 0 | 0
0 | 0 | 126.8692 | 0 | 0 | 0 | 0
0 | 0 | 0 | 218.4688 | 0 | 0 | 0
0 | 0 | 0 | 0 | 294.0186 | 0 | 0
0 | 0 | 0 | 0 | 0 | 119.622 | 0
0 | 0 | 0 | 0 | 0 | 0 | 32.2454
A11'
60.0176 | 0 | 0 | 0 | 0 | 0 | 0
0 | 294.0848 | 0 | 0 | 0 | 0 | 0
0 | 0 | 126.8692 | 0 | 0 | 0 | 0
0 | 0 | 0 | 218.4688 | 0 | 0 | 0
0 | 0 | 0 | 0 | 294.0186 | 0 | 0
0 | 0 | 0 | 0 | 0 | 119.622 | 0
0 | 0 | 0 | 0 | 0 | 0 | 32.2454
N * A11'
120.0353 | 0 | 0 | 0 | 0 | 0 | 0
0 | 588.1696 | 0 | 0 | 0 | 0 | 0
0 | 0 | 253.7385 | 0 | 0 | 0 | 0
0 | 0 | 0 | 436.9376 | 0 | 0 | 0
0 | 0 | 0 | 0 | 588.0372 | 0 | 0
0 | 0 | 0 | 0 | 0 | 239.2439 | 0
0 | 0 | 0 | 0 | 0 | 0 | 64.4907
R = inversa de (N * A11')
0.0083309 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0.0017002 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0.0039411 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0.0022887 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0.0017006 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0.0041798 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0.015506
M= A21 / (N A11')
0.0083309 | -0.0017002 | 0 | 0 | -0.0017006 | 0 | 0
0 | 0.0017002 | 0.0039411 | 0 | 0 | 0 | 0
0 | 0 | -0.0039411 | 0.0022887 | 0 | 0 | 0
0 | 0 | 0 | -0.0022887 | 0.0017006 | 0.0041798 | 0
0 | 0 | 0 | 0 | 0 | -0.0041798 | 0.015506
C =A21 / (N A11') * A12
0.011732 | -0.0017002 | 0 | -0.0017006 | 0
-0.0017002 | 0.0056413 | -0.0039411 | 0 | 0
0 | -0.0039411 | 0.0062297 | -0.0022887 | 0
-0.0017006 | 0 | -0.0022887 | 0.0081691 | -0.0041798
0 | 0 | 0 | -0.0041798 | 0.019686
B= Inversa negativa de A21 / (N A11') * A12
-102.604 | -75.7003 | -64.0939 | -44.1078 | -9.3652
-75.7003 | -410.1374 | -300.6763 | -112.1843 | -23.8196
-64.0939 | -300.6763 | -402.7388 | -141.5527 | -30.0553
-44.1078 | -112.1843 | -141.5527 | -192.1252 | -40.7931
-9.3652 | -23.8196 | -30.0553 | -40.7931 | -59.4591
A11 * Q |  | A10 * H0 |  | S= A11 Q + A10 H0
6.403 |  | -100 |  | -93.597
10.739 |  | 0 |  | 10.739
0.44193 |  | 0 |  | 0.44193
7.3151 |  | 0 |  | 7.3151
2.99 |  | 0 |  | 2.99
6.3775 |  | 0 |  | 6.3775
3.0089 |  | -100 |  | -96.9911
M * S |  | A21 * Q |  | C = (M * S) (A21 *Q - q)
-0.80309 |  | 0.06 |  | -0.80309
0.02 |  | 0.04 |  | 0.02
0.015 |  | 0.03 |  | 0.015
0.015 |  | 0.03 |  | 0.015
-1.5306 |  | 0.04 |  | -1.5306
H i+1 = B * C
93.5975
82.8569
83.2982
90.612
96.9907
A12 H |  | T= A12 H + A10 H0 |  | W= R * T
93.5975 |  | -6.4025 |  | -0.053338
-10.7406 |  | -10.7406 |  | -0.018261
-0.44123 |  | -0.44123 |  | -0.0017389
-7.3139 |  | -7.3139 |  | -0.016739
-2.9855 |  | -2.9855 |  | -0.0050771
-6.3787 |  | -6.3787 |  | -0.026662
96.9907 |  | -3.0093 |  | -0.046662
Y= R * A11
0.5 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0.5 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0.5 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0.5 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0.5 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0.5 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0.5
L= I-Y
0.5 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0.5 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0.5 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0.5 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0.5 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0.5 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0.5
X= L* A11 Q |  | Qi+1 |  | dq=Qi+1 – Qi
0.053343 |  | 0.10668 |  | -4.8681e-06
0.018258 |  | 0.036519 |  | 2.7521e-06
0.0017417 |  | 0.0034806 |  | -2.7521e-06
0.016742 |  | 0.033481 |  | -2.7521e-06
0.0050847 |  | 0.010162 |  | -7.6201e-06
0.026657 |  | 0.053319 |  | 4.8681e-06
0.046657 |  | 0.093319 |  | 4.8681e-06